## Sheet1
Name of Device |  | ID | Function |  | Type | Input | Output | Location |  | Notes
Mech Panel Power |  | MP-Elec | measures elec- Mech Panel |  |  | ? | ? | Need ENV rec
HP Power |  | HP-Elec | measures elec used by HP |  |  | ? | ? | Need ENV rec.
Weather Forecast |  | Weather | Retrieves weather data |  |  | ? | ? | Need ENV rec
Snow-Moisture? |  | Snow-W | Moisture Present on Entry? |  | ETI pole sensor |  |  | elevated- near slab
Snow-Freezing? |  | Snow-T | Freezing Temp on Entryway? |  | temp sensor |  | 10K thermis | sensor well entry slab
Pump 1 |  | P1 | HP EHE/Geo Loop |  | 120volt Magna |  |  | Mech Panel
Pump 2 |  | P2 | HP Load |  | 120volt Magna |  |  | Mech Panel
Pump 3 |  | P3 | Flat Plate Exch Load |  | 120volt Alpha |  |  | Mech Panel
Pump 4 |  | P4 | Flat PlateExc |  | 120volt Alpha |  |  | Mech Panel
Pump 5 |  | P5 | chilled water to HVAC coil |  | 120volt Alpha |  |  | Mech Panel
Pump 6 |  | P6 | hot/chilled water to Wave |  | 120volt Alpha |  |  | Mech Panel
Pump 7 |  | P7 | DHW to tank from HP |  | 120volt Alpha |  |  | HP |  | may be controlled by HP
Zone Valve A |  | ZVA | Mixes water temp to Wave |  | motorized ZV | 24 volt |  | Mech Panel |  | normally closed, opens when chilled water is sent to Wave
Zone Valve B |  | ZVB | bypasses fluid to rad zones |  | motorized ZV | 24 volt |  | Mech Panel |  | normally closed, opens when fluid is sent to HVAC coil or Wave
Grundfos VFS 2-40 (1) |  | Coil Flow | Measures flow to HVAC coil |  | flow sensor |  | .5-3.5 volts | Mech Panel
Grundfos VFS 2-40 (1) |  | Coil T-Out | Measures temp f. HVAC coil |  | temp sensor |  | .5-3.5 volts | Mech Panel
HVAC fluid sensor (S1) |  | Coil T-In | Measures temp to HVAC coil |  | temp sensor |  | 10K thermis | Mech Panel
Grundfos VFS 2-40 (2) |  | Wave Flow | Measures flow to Wave | from Wave | flow sensor |  | .5-3.5 volts | Mech Panel
Grundfos VFS 2-40 (2) |  | Wave T-Out | Measures temp from Wave |  | temp sensor |  | .5-3.5 volts | Mech Panel
Wave fluid temp sensor (S2) |  | Wave T-In | Measures temp to Wave |  | temp sensor |  | 10K thermis | Mech Panel
Grundfos VFS 5-100 | 5-100 (S3) | EHE Flow | Measures flow to EHE/GE | f. EHE/Geo | flow sensor |  | .5-3.5 volts | Mech Panel
Grundfos VFS 5-100 (3) |  | EHE T-Out | Meaures temp f. EHE/Geo |  | temp sensor |  | .5-3.5 volts | Mech Panel
EHE/Geo temp sensor (S3) |  | EHE T-In | Measures temp to EHE/Geo |  | temp sensor |  | 10K thermis | Mech Panel
Grundfos VFS 5-100 (4) |  | Load Flow | Measures load flow to HP |  | flow sensor |  | .5-3.5 volts | Mech Panel
Grundfos VFS 5-100 (4) |  | Load T-In | Measures load temp to HP |  | temp sensor |  | .5-3.5 volts | Mech Panel
Load Output Sensor (S4) |  | Load T-Out | Measures load temp from HP |  | temp sensor |  | 10K thermis | Mech Panel
Grundfos VFS5-100 (5) |  | EHE Flow Ex | Measures EHE flow thr HtExc |  | flow sensor |  | .5-3.5 volts | Mech Panel
Grundfos VFS 5-100 (5) |  | EHE Ex T-Out | Measures EHE temp f HtExc |  | temp sensor |  | .5-3.5 volts | Mech Panel
EHE exit temp f HtExch | f Ht.Exch (S5) | EHE Ex T-In | Measures EHE exit f HtExch |  | temp sensor |  | 10K thermis | Mech Panel
Grundfos VFS 5-100 (6) |  | Load Flow Ex | Measures Load flow thr HtEx |  | flow sensor |  | .5-3.5 volts | Mech Panel
Grundfos VFS 5-100 (6) (S6) | 5-100 (6) | Load Ex T-Out | Measures Load temp f HtEx |  | temp sensor |  | .5-3.5 volts | Mech Panel
Tekmar Valve |  | Tekmar (1) | Diverts EHE fluid flow |  | motorized V | 24 volt
Load In temp to Ht.Exch | to HtExc (S6) | Load Ex T-In | Measures Load temp t HtEx |  | temp sensor |  | 10K thermis | Mech Panel
Axial Blower for HVAC |  | Blower 1 | boosts air volume for A.C. |  | variable speed 120 volt |  |  | On HVAC/ERV system
Motorized Vent |  | M-Vent | allows int. air to HVAC coil |  | open/closed | 24 volt (?) |  | N.C. except when call for A.C.
East EHE Wall Temperature |  | T-EHE-E | Measures temp of East EHE |  | temp sensor |  | 10K thermis | W EHE sensor well
SE EHE Wall Temperature |  | T-EHE-SE | Measures temp of SE EHE |  | temp sensor |  | 10K thermis | SE EHE sensor well
SW EHE Wall Temperature |  | T-EHE-SW | Measures temp of SW EHE |  | temp sensor |  | 10K thermis | SW EHE sensor well
West EHE Temperature |  | T-EHE-West | Measures temp of West EHE |  | temp sensor |  | 10K thermis | West EHE sensor well
NW EHE Wall Temperature |  | T-EHE-NW | Measures temp of NW EHE |  | temp sensor |  | 10K thermis | NW EHE sensor well
NE EHE Wall Temperature |  | T-EHE-NE | Measures temp of NE EHE |  | temp sensor |  | 10K thermis | NE EHE sensor well
East EHE Zone Valve |  | ZV-EHE-E | Controls flow to East EHE |  | motorized ZV | 24 volt |  | East EHE area N.C. fully open on demand
SE EHE Zone Valve |  | ZV-EHE-SE | Controls flow to SE EHE |  | motorized ZV | 24 volt |  | SE EHE area | N.C. fully open on demand
SW EHE Zone Valve |  | ZV-EHE-SW | Controls flow to SW EHE |  | motorized ZV | 24 volt |  | SW EHE area N.C. fully open on demand
West EHE Zone Valve |  | ZV-EHE-W | Controls flow to West EHE |  | motorized ZV | 24 volt |  | West EHE area N.C. fully open on demand
NW EHE Zone Valve |  | ZV-EHE-NW | Controls flow to NW EHE |  | motorized ZV | 24 volt |  | NW EHE area | N.C. fully open on demand
NE EHE Zone Valve |  | ZV-EHE-NE | Controls flow to NE EHE |  | motorized ZV | 24 volt |  | NE EHE area N.C. fully open on demand
Domestic Hot Water Temp |  | DHW-Temp | Measures temp of DHW |  | temp sensor |  | 10K thermis | DHW storage tank
Temperature of Zone 1 |  | Zone 1 Temp | Measures temp of Zone 1 |  | temp sensor |  | 10K thermis | Zone 1
Temperaure of Zone 2 |  | Zone 2 Temp | Measures temp of Zone 2 |  | temp sensor |  | 10K thermis | Zone 2
Temperature of Zone 3 |  | Zone 3 Temp | Measures temp of Zone 3 |  | temp sensor |  | 10K thermis | Zone 3
Temperature of Zone 4 |  | Zone 4 Temp | Measures temp of Zone 4 |  | temp sensor |  | 10K thermis | Zone 4
Temperature of Zone 5 |  | Zone 5 Temp | Measures temp of Zone 5 |  | temp sensor |  | 10K thermis | Zone 5
Temperature of Zone 6 |  | Zone 6 Temp | Measures temp of Zone 6 |  | temp sensor |  | 10K thermis | Zone 6
Temperature of Zone 7 |  | Zone 7 Temp | Measures temp of Zone 7 |  | temp sensor |  | 10K thermis | Zone 7
Temperature of Zone 8 |  | Zone 8 Temp | Measures temp of Zone 8 |  | temp sensor |  | 10K thermis | Zone 8
Temperature of Zone 9 |  | Zone 9 Temp | Measures temp of Zone 9 |  | temp sensor |  | 10K thermis | Zone 9
Temperature of Zone 10 |  | Zone 10 Temp | Measures temp of Zone 10 |  | temp sensor |  | 10K thermis | Zone 10
Temperature of Wave Zone |  | Wave Z Temp | Measures temp of Wave Z |  | temp sensor |  | 10K thermis
Radiant Zone 1 |  | ZV1 | Controls flow to Zone 1 |  | motorized ZV | 24 volt |  | Zone 1 | N.C. fully open on demand
Radiant Zone 2 |  | ZV2 | Controls flow to Zone 2 |  | motorized ZV | 24 volt |  | Zone 2 | N.C. fully open on demand
Radiant Zone 3 |  | ZV3 | Controls flow to Zone 3 |  | motorized ZV | 24 volt |  | Zone 3 | N.C. fully open on demand
Radiant Zone 4 |  | ZV4 | Controls flow to Zone 4 |  | motorized ZV | 24 volt |  | Zone 4 | N.C. fully open on demand
Radiant Zone 5 |  | ZV5 | Controls flow to Zone 5 |  | motorized ZV | 24 volt |  | Zone 5 | N.C. fully open on demand
Radiant Zone 6 |  | ZV6 | Controls flow to Zone 6 |  | motorized ZV | 24 volt |  | Zone 6 | N.C. fully open on demand
Radiant Zone 7 |  | ZV7 | Controls flow to Zone 7 |  | motorized ZV | 24 volt |  | Zone 7 | N.C. fully open on demand
Radiant Zone 8 |  | ZV8 | Controls flow to Zone 8 |  | motorized ZV | 24 volt |  | Zone 8 | N.C. fully open on demand
Radiant Zone 9 |  | ZV9 | Controls flow to Zone 9 |  | motorized ZV | 24 volt |  | Zone 9 | N.C. fully open on demand
Radiant Zone 10 |  | ZV10 | Controls flow to Zone 10 |  | motorized ZV | 24 volt |  | Zone 10 | N.C. fully open on demand
Wave Zone |  | ZV11 | Controls flow to Wave |  | motorized ZV | 24 volt |  | Wave Air T | N.C. fully open on demand
Humidity Sensor |  | Humidity 1 | Measures humidity |  | Humidty sensor |  |  | Kitchen | Need rec model from ENV